Drinking Water Distribution System Sampling Plan (DSSP)

Instructions to System

These instructions and template are provided by the New Mexico Environment Department (NMED) Drinking Water Bureau (DWB) as a guide for water systems that are revising or developing their distribution system sampling plan (DSSP).  The DWB will use this template when providing technical assistance to systems revising or developing their DSSP and when reviewing these plans for system compliance or capacity assessments.

The DWB requires that drinking water systems maintain and implement a DWB-approved distribution system sample plan (DSSP) that reflects current regulatory requirements and system conditions, and enables certified samplers or operators to collect all routine and repeat compliance distribution system samples according to sample schedules established by the DWB.  The DSSP is also required to be included as an appendix in the system’s Operation and Maintenance Plan.  A general guideline to follow when developing or revising your DSSP is:

the plan needs to be specific enough that any certified sampler or operator could take the plan without any prior knowledge of your system and accurately implement it.

At a minimum, the DSSP must include:

- A written description of the system

  - Can be the same one you use for both your Operation and Maintenance Plan and your Emergency Response Plan

- High quality and accurate map(s) of the distribution system showing the general layout of all system features and all sample sites

  - Bacteriological

    - Routine

    - Repeats

    - Triggered source(s)

  - Chlorine residual (if a chlorinated system)

  - Lead and copper (if required by regulation)

  - Disinfection By-Products (DBPs) (if required by regulation)

  - Asbestos (if required by regulation)

  - Turbidity (if required by regulation)

  - You may want to consider separate maps for specific groups of samples to keep any one map from getting too cluttered; i.e.,

    - 1 map for bacteriological and chlorine residual

    - 1 map for lead and copper and asbestos

    - 1 map for DBPs

    - 1 map for turbidity and TOC

- A written description of each sample site including:

  - contact info

  - location and directions

  - access info

  - sample(s) collected at each location

  - any other info required to get to the site and safely access and use the sample tap

- The name(s) of each laboratory the system uses for sample analysis

  - For a list of labs under contract with the DWB and approved to use NM Water Conservation Fee funds for routine compliance samples go to https://www.env.nm.gov/dwb/index.htm and follow the links for sample collection and approved labs

- Review and approval by DWB

Keep in mind that your DSSP is a living document and should be updated to reflect changes at your Public Water System (PWS) such as:

- Regulatory changes that involve distribution system sampling

- Major changes in population

- A new or additional source

- Infrastructure changes such as

  - A change in the distribution system pressure zones or extended/abandoned lines

  - Changes in storage

  - Changes in disinfection

  - Treatment changes

The template is organized with a title page, a revisions tracking page, a table of contents, the body and appendices for support documents.  Please note that all items within the body of the plan may not apply to your water system (such as asbestos or disinfection by-product sampling), some items may be included as standard operating procedures (SOPs), as appendices or in multiple locations (provide once and reference back to original location).

Similarly, all appendices may not apply.  For those that don’t apply you can either delete all reference to them in the plan and reorder the remaining ones, or you can designate “N/A” next to any appendices titles in the table of contents that don’t apply, leave the references in the body of the plan as they are and include all appendix title pages.  Those that are “N/A” will serve as place-holders.

Each section of the template has been formatted with some fundamental structure and information to help guide you in your write-up.  You are welcome to copy & paste as long as the information you provide in your system’s plan accurately represents your system.  You are also welcome to change the formatting for your purposes, but keep in mind that your plan will be evaluated based on the information outlined in these instructions and requested in each section of the template.

General Information

In January 2011 the NMED DWB transferred all drinking water distribution system sampling from the DWB sample collectors to the water system for bacteriological, chlorine residual, lead, copper, the disinfection by-products (DBPs) total trihalomethanes (TTHMs) and haloacetic acids (HAA5s), asbestos and turbidity (if a surface water or ground water under direct influence of surface water (GWUDI) system).  Prior to this change, DWB samplers would collect all routine chemical compliance samples (except lead and copper) from distribution as well as source and Entry Point(s).

Previous changes required by the Ground Water Rule (GWR) incorporated system facility ID numbers and sampling point ID numbers onto lab forms.  Facility ID numbers can be found by using the ‘Water System Facilities’ link from the water system detail page for your water system from Drinking Water Watch; https://dww.water.net.env.nm.gov/DWW/.  Sampling point ID numbers can be found by clicking on each specific facility ID number.

The DWB provides general sample schedule information for each Public Water System (PWS).  That schedule can be found by using the ‘Sample Schedules’ link from the water system detail page for your water system from Drinking Water Watch; https://dww.water.net.env.nm.gov/DWW/.  In addition, system-specific sampling information, more detailed schedules and PWS sample tracking is available through the DWB online sampling tool.  To use the online sampling tool you must have a current NM operator or sampler certification and be registered with an appropriate PWS(s) in the NM Utility Operator Certification Program (UOCP) Database.  To download instructions on how to register and use the tool go to https://www.env.nm.gov/dwb/sampling/documents/DrinkingWaterSampleCollectionApplication.pdf.

The following sections provide specific guidance for each individual or group of samples you are required to collect from your distribution system.  You will be expected to address this guidance when developing or revising your DSSP, and your DWB Compliance Officer (CO) will be using these instructions and the template to review your plan.

Bacteriological Sampling under the Revised Total Coliform Rule (RTCR)

The RTCR will take effect on April 1, 2016. This rule revises the Total Coliform Rule (TCR) and will require DWB-approved modifications to existing DSSPs currently in use by PWSs.

All Systems

Under the RTCR, your DSSP must address the following requirements and include the following information:

- Your system’s bacteriological sample collection schedule

  - All systems will be required to collect routine bacteriological samples on a monthly basis

    - All reduced (quarterly) sampling has been eliminated

  - PWSs that collect more than one sample per month (systems serving 1001 or more people) must collect samples at regular intervals throughout the month, EXCEPT

  - Ground water systems serving 4900 or fewer people (5 routine samples or fewer per month) may collect all required samples on a single day if they are taken from different sites

- All sample sites including locations for routine, repeat, triggered source and ‘special’ seasonal start-up sampling

  - Sample sites must be located in accessible locations and be representative of water quality throughout the distribution system

    - At a customer’s premise

    - Dedicated sampling station

    - Other designated compliance sample site

  - For all routine Total Coliform positive (TC+) samples all systems are required to collect three (3) repeat samples for every TC+ from locations designated on DSSP

    - Original sample location

    - Upstream within 5 service connections

    - Downstream within 5 service locations

    - System may use alternate up- and downstream repeat sampling locations if they will be more representative of system conditions

      - Use of alternate repeat sampling locations must be based on an SOP approved by the system’s DWB Compliance Officer (CO)

  - Repeat sample locations must also include all active sources that will be sampled as untreated triggered sources under the Ground Water Rule (GWR)

    - The DWB will not allow a triggered source water sample under the Ground Water Rule (GWR) to count as one of the distribution system repeats under the RTCR

  - Seasonal systems are systems that start up and shut down at the beginning and end of a specific operating season and may depressurize all or part of the water system at some point during the year

    - These systems are required to follow specific start-up procedures and prior to serving water certify that these procedures have been completed

    - The start-up procedure will require the system to collect one or more ‘special’ microbiological samples to verify water quality

      - ‘Special’ samples are samples collected and paid for by the water system

Remember that all bacteriological samples (routine compliance, repeats, specials) must be sealed with red evidentiary tape and include chain-of-custody verification on the laboratory forms.  Further, labs are instructed to reject any samples not collected by a certified sampler or operator.

The DWB is requiring systems to designate their minimum number of monthly routine sampling sites based on the following Table 1:

| Population | Minimum Number of Samples per Month Required by RTCR | Minimum Number of Routine Sample Sites Required on Sampling Plan |
| --- | --- | --- |
| 25 to 1000 | 1 | 4 |
| 1001 to 2500 | 2 | 8 |
| 2501 to 3300 | 3 | 9 |
| 3301 to 4100 | 4 | 12 |
| 4101 to 4900 | 5 | 15 |
| 4901 to 5800 | 6 | 18 |
| 5801 to 6700 | 7 | 21 |
| 6701 to 7600 | 8 | 24 |
| 7601 to 8500 | 9 | 27 |
| Population | Minimum Number of Samples per Month Required by RTCR | Minimum Number of Routine Sample Sites Required on the DSSP |
| 8501 to 12,900 | 10 | 30 |
| 12,901 to 17,200 | 15 | 30 |
| 17,201 to 21,500 | 20 | 40 |
| 21,501 to 25,000 | 25 | 50 |
| 25,001 to 33,000 | 30 | 60 |
| 33,001 to 41,000 | 40 | 60 |
| 41,001 to 50,000 | 50 | 75 |
| 50,001 to 59,000 | 60 | 90 |
| 59,001 to 70,000 | 70 | 105 |
| 70,001 to 83,000 | 80 | 120 |
| 83,001 to 96,000 | 90 | 135 |
| 96,001 to 130,000 | 100 | 150 |
| 130,001 to 220,000 | 120 | 180 |
| 220,001 to 320,000 | 150 | 225 |
| 320,001 to 450,000 | 180 | 270 |
| 450,001 to 600,000 | 210 | 315 |
| 600,001 to 780,000 | 240 | 360 |
| 780,001 to 970,000 | 270 | 405 |
| 970,001 to 1,230,000 | 300 | 450 |
| 1,230,001 to 1,520,000 | 330 | 495 |
| 1,520,001 to 1,850,000 | 360 | 540 |
| 1,850,001 to 2,270,000 | 390 | 585 |
| 2,270,001 to 3,020,000 | 420 | 630 |
| 3,020,001 to 3,960,000 | 450 | 675 |
| 3,960,001 or more | 480 | 720 |

That minimum number of monthly routine sites required on the DSSP increases the RTCR population-required minimums by the following Table 2 factors:

| Population Range | Minimum Number of Samples per Month Required by RTCR | Multiplier to Obtain Minimum Number of Routine Sample Sites Required on the DSSP |
| --- | --- | --- |
| 25 to 2500 | 1 - 2 | 4 |
| 2501 to 12,900 | 3 - 10 | 3 |
| 12,901 to 33,000 | 15 - 30 | 2 |
| 33,001 or more | 40 - 480 | 1.5 |

This multiplier gives the system more DSSP-designated sample locations to choose from each month.  These additional sample locations provide the system flexibility to avoid locations that may have been adversely impacted by line work, hydrant events (fire, flushing) or other activities that could have created a potential pathway for contamination into that section of the distribution system while still collecting representative samples from designated locations.

Systems are required to designate the physical address for each monthly routine and repeat sample location using the following Figure 1 example spreadsheet:

Systems will first select their PWS from the drop down alphabetical list of all PWS in NM.  Once the PWS name is selected the spreadsheet will automatically populate with PWS # and population, and number of required sample sites, routine sample site names and repeat sample site names based on the population multiplier.  The system is required to enter the physical address or physical location for each routine (RTxxx) & standard repeat site (RPxxxO, RPxxxU and RPxxxD) in the spreadsheet.

Note that systems can use alternate up- or downstream repeat sampling locations that are outside the five (5) connections from the original sample site.  The DWB will NOT require systems to designate an address or location for these alternate up- or downstream repeat sites; RPxxxUA and RPxxxDA address cells in spreadsheet are locked.  Instead, the DWB will require the system to specify their criteria for selecting these alternate repeat sampling sites on a situational basis in a standard operating procedure (SOP) provided in the DSSP.  The system must design the SOP to focus the repeat samples at locations that best verify and determine the extent of potential contamination of the distribution system area based on specific situations; however, the DWB may modify the SOP or require other alternate monitoring locations as needed.

The DWB will be verifying that the PWS is sampling from each routine and repeat sample location designated on their DSSP.  Your Compliance Officer will also verify that the system is collecting the routine samples at regular intervals from month to month (i.e., same week each month) and is rotating through each major and minor portion of the distribution system every fourth month.  This means that in general, a system could use the same sample locations for January/April/July/October, a second set of locations for February/May/August/November and a third set for March/June/September/December as long as this rotation provides representative sampling of the entire distribution system.

Exceptions to the increased number of routine sampling locations based on the population range multiplier, sample rotation and alternate repeat SOP criteria will be applied to those systems with only one tap.  These are typically transient, noncommunity systems such as campgrounds.  These systems will be required to use that one tap every month for their routine sampling site.  All three (3) repeats will also be sampled from that one tap.  The water system will be allowed to collect the required set of repeat samples over a three-day period or to collect a larger volume repeat sample(s) in one or more sample containers of any size, as long as the total volume collected is at least 300 ml.

Systems with just two (2) taps will be required to alternate between each of those taps for their routine monthly sampling.  One of those taps will more than likely be either in an up- or downstream location and will be sampled accordingly as a repeat.  The other tap will be sampled twice over a two-day period or to collect a larger volume repeat sample(s) in one or more sample containers of any size, as long as the total volume collected is at least 200 ml.

The following RTCR guidance documents can be downloaded from https://www.env.nm.gov/dwb/index.htm:

- RTCR Sample Sites Spreadsheet

- Requirements for Small Systems Fact Sheet

- Repeat Monitoring Requirements for Small Systems Fact Sheet

- Requirements for Seasonal Systems Fact Sheet

- Seasonal System Start-Up Procedure Guidance and Checklist

- Level 1 and Level 2 Assessments and Corrective Actions Fact Sheet

- Level 1 Assessment and Corrective Action Form

- Level 2 Assessment and Corrective Action Form

- List of Sanitary Defects

- Large System Guidance

- Training Presentation Slides (as handouts in pdf)

- DSSP Template & Instructions (https://www.env.nm.gov/dwb/tools/Index.htm)

Chlorine Residual Monitoring

Best management practices recommend that operators monitor chlorine residuals throughout their distribution systems on a regular basis.  This is to ensure that injection dosages are sufficient to meet chlorine demand and maintain adequate residuals in the vulnerable portions of the distribution system.  Vulnerable sections are anywhere you have increased water age or stagnant water (storage tanks, dead ends, low occupancy areas).  This monitoring goes beyond the chlorine residual measurements you take when collecting your monthly routine bacteriological samples.  Keep in mind though that elevated residuals combined with prolonged water age can lead to the formation of harmful disinfection by-products (DBPs), total trihalomethanes (TTHMs) and haloacetic acids (HAA5s).  Your DSSP needs to include all chlorine residual monitoring locations that you use – those associated with your monthly routine bacteriological sampling and those you use for disinfection process control.

The DWB is requiring systems to designate their minimum number of monthly chlorine monitoring sites based on the following table:

| Population | Minimum Number of Sites per Month based on Population | Minimum Number of Chlorine Monitoring Sites Required on Sampling Plan |
| --- | --- | --- |
| 25 to 1000 | 1 | 4 |
| 1001 to 2500 | 2 | 8 |
| 2501 to 3300 | 3 | 9 |
| 3301 to 4100 | 4 | 12 |
| 4101 to 4900 | 5 | 15 |
| 4901 to 5800 | 6 | 18 |
| 5801 to 6700 | 7 | 21 |
| 6701 to 7600 | 8 | 24 |
| 7601 to 8500 | 9 | 27 |
| 8501 to 12,900 | 10 | 30 |
| 12,901 to 17,200 | 15 | 30 |
| 17,201 to 21,500 | 20 | 40 |
| 21,501 to 25,000 | 25 | 50 |
| 25,001 to 33,000 | 30 | 60 |
| 33,001 to 41,000 | 40 | 60 |
| 41,001 to 50,000 | 50 | 75 |
| 50,001 to 59,000 | 60 | 90 |
| 59,001 to 70,000 | 70 | 105 |
| 70,001 to 83,000 | 80 | 120 |
| 83,001 to 96,000 | 90 | 135 |
| 96,001 to 130,000 | 100 | 150 |
| 130,001 to 220,000 | 120 | 180 |
| 220,001 to 320,000 | 150 | 225 |
| 320,001 to 450,000 | 180 | 270 |
| 450,001 to 600,000 | 210 | 315 |
| 600,001 to 780,000 | 240 | 360 |
| 780,001 to 970,000 | 270 | 405 |
| 970,001 to 1,230,000 | 300 | 450 |
| 1,230,001 to 1,520,000 | 330 | 495 |
| 1,520,001 to 1,850,000 | 360 | 540 |
| 1,850,001 to 2,270,000 | 390 | 585 |
| 2,270,001 to 3,020,000 | 420 | 630 |
| 3,020,001 to 3,960,000 | 450 | 675 |
| 3,960,001 or more | 480 | 720 |

That minimum number of monthly monitoring sites required on the DSSP increases the population-required minimums by the following factors:

| Population Range | Minimum Number of Samples per Month Required by Population | Multiplier to Obtain Minimum Number of Routine Monitoring Sites Required on the DSSP |
| --- | --- | --- |
| 25 to 2500 | 1 - 2 | 4 |
| 2501 to 12,900 | 3 - 10 | 3 |
| 12,901 to 33,000 | 15 - 30 | 2 |
| 33,001 or more | 40 - 480 | 1.5 |

This multiplier gives the system more DSSP-designated chlorine monitoring locations to choose from each month.  These additional monitoring locations provide the system flexibility to avoid locations that may have been adversely impacted by line work, hydrant events (fire, flushing) or other activities that could have created an unrepresentative chlorine residual in that section of the distribution system.

Remember that the Stage 1 Disinfectants/Disinfection By-Products Rule (S1DBPR) established a Maximum Residual Disinfectant Limit (MRDL) for chlorine of 4 mg/L, and requires systems to submit quarterly chlorine residual reports to their DWB CO.  A copy of that disinfectant residual report can be found in Appendix A of these instructions.  Include this report in Appendix E of your DSSP.

Lead and Copper Rule (LCR) Sampling

Lead and copper is typically not a source water issue; these contaminants are usually present as a result of chemical leaching from system or customer plumbing.  The main objective for the LCR is to protect the public from these contaminants resulting from corrosion in the system or customer’s pipes.  Protocol requires that these samples are:

- Point-of-Use (POU) collected directly from the customer’s tap

- Collected as a “first draw” sample before any other usage takes place at the sampling tap (no flushing of faucet or lines before collection)

- 6 to 18 hours water age in customer’s plumbing

- Typically collected by occupant of sampling location

- Typically collected during third quarter warm weather months July to September

The number of LCR samples you are required to collect is determined by the DWB and is based on population served.  You can determine your sample requirements by referencing your PWS sample schedule on Drinking Water Watch (https://dww.water.net.env.nm.gov/DWW/) or by accessing the DWB online sampling tool.

Use the following LCR tier structure to determine where you need to sample; designate these locations on your DSSP.  The tier structure is based on your type of system and the age and types of structures you have in your community.

| LCR TIER STRUCTURE |  |  |  |
| --- | --- | --- | --- |
| Community (CWS) |  | Non Transient Non-Community (NTNCWS) |  |
| Structures that have copper pipes with lead solder or lead pipes and/or served by lead service lines |  |  |  |
| Tier 1 | single family structures installed 1983 through 1985; or multi-family structures (1983-1985) that make up > 20% of total service connections | Tier 1 | any structure installed from 1983 through 1985 |
| Tier 2 | multi-family structures installed by 1983 and after that make up 20% or less of total service connections | Tier 2 | N/A |
| Tier 3 | single family structures installed by 1982 or before | Tier 3 | any structure installed by 1982 or before |
| Other | structures with other plumbing materials | Other | structures with other plumbing materials |

General guidelines for lead and copper site selection, sampling and reporting are provided in Appendix B of these instructions.  Include these guidelines in Appendix F of your DSSP.

Disinfectants/Disinfection By-Products (D/DBP) Sampling

Disinfection byproducts (DBPs) form when water that contains natural organic matter (NOM) is mixed with certain forms of chlorine.  NOM, considered a DBP precursor, results from the decomposition of plant and animal material and is most commonly found in surface water or ground water under direct influence of surface water (GWUDI) where this organic matter frequently enters the water body from runoff.  All public water systems using surface water must disinfect the water prior to delivery to the first customer, thereby bringing the NOM in contact with chlorine (the most commonly used disinfectant).  DBPs are harmful to human health and are regulated under the Stage 1 and 2 Disinfectants/Disinfection By-Products Rule (S1/2 D/DBPR) of the Safe Drinking Water Act (SDWA).

DBPs generally continue to form over time so typically, the highest concentrations are found in distribution where the "oldest" water is found; this is where sampling locations are chosen (though DBPs can sometimes degrade with time).  Other factors that influence DBP formation include pH (higher pH favors total trihalomethane production, lower pH favors haloacetic acid production) and temperature (higher temperature favors DBP production).  This is why the third quarter of the year (July-September) is usually designated for DBP sampling for systems required to collect only 1 set of DBP samples per year.

The DWB fully implemented the Stage 2 D/DBP Rule on October 1, 2013 for community and non-transient non-community water systems (CWS and NTNCWS) that produce or deliver water that is treated with a primary disinfectant (chlorine).  That implementation included sending correspondence to each regulated system that described the number and general location of each type of DBP sample, Total Trihalomethane (TTHM) and Haloacetic Acid (HAA5) the system is required to collect.  Numbers and locations vary depending on whether your system uses ground water (GW) or surface water (SW), and population served, as follows:

- Certain GW or SW systems serving less than 500 population were instructed to collect one (1) DBP2 sample per year from their distribution system during a specific month

  - A DBP2 sample means that both the TTHM and HAA5 samples are to be collected from the same distribution system sample location

  - The letter included a Sample Location Identification Checklist (SLIC) entitled “Distribution Sampling Location” that the water system was instructed to use to designate the distribution system sample location for the DBP2 samples

  - An example of this correspondence and the SLIC are included in Appendix C of these instructions

- Other GW or SW systems serving less than 500 population were instructed to collect one (1) TTHM-IND and one (1) HAA5-IND sample per year from their distribution system during a specific month

  - A TTHM-IND and HAA5-IND sample means that the TTHM sample is collected from one location and the HAA5 sample is collected from a different and separate location

  - The letter included a SLIC that the water system was instructed to use to designate the two (2) separate distribution system sample locations for the TTHM-IND and HAA5-IND samples

  - An example of this correspondence and the SLIC are included in Appendix D of these instructions

- GW systems serving 500-9999 population were instructed to collect one (1) TTHM-1 Dual and one (1) HAA5-1 Dual sample per year from their distribution system during a specific month

  - A TTHM-1 Dual and HAA5-1 Dual sample means that both TTHM and HAA5 samples are collected at the same time and location from two (2) different locations within distribution

  - The letter included a SLIC that the water system was instructed to use to designate the two (2) separate distribution system sample locations for the TTHM-1 Dual and HAA5-1 Dual samples

  - An example of this correspondence and the SLIC are included in Appendix E of these instructions

- SW systems serving 500-3300 population were instructed to collect one (1) TTHM-IND and one (1) HAA5-IND sample per quarter

  - A TTHM-IND and HAA5-IND sample means that the TTHM sample is collected from one location and the HAA5 sample is collected from a different and separate location

  - Quarterly samples must be collected at regular intervals

    - January, April, July and October, or

    - February, May, August and November, or

    - March, June, September and December

  - The letter included a SLIC that the water system was instructed to use to designate the two (2) separate distribution system sample locations for the TTHM-IND and HAA5-IND samples

  - An example of this correspondence and the SLIC are included in Appendix F of these instructions

- SW systems serving 3301-9999 population were instructed to collect one (1) TTHM-1 Dual and one (1) HAA5-1 Dual sample per quarter

  - A TTHM-1 Dual and HAA5-1 Dual sample means that both TTHM and HAA5 samples are collected at the same time and location from two (2) different locations within distribution

  - Quarterly samples must be collected at regular intervals

    - January, April, July and October, or

    - February, May, August and November, or

    - March, June, September and December

- All other GW and SW systems serving 10,000 and greater population were instructed to collect anywhere from 4 to 20 Dual TTHM and HAA5 samples per quarter

  - Dual sampling means that both TTHM and HAA5 samples are collected at the same time and location quarterly

  - Sample locations are designated DBP-1 through 5, TTHM -1 through 8 and HAA5-1 through 7

    - DBP-1 through 5 are the distribution system sample locations the system has been using from the Stage 1 D/DBPR – they remain in use

    - TTHM-1 through 8 and HAA5-1 through 7 are new sample locations for S2 D/DBPR

  - Refer to Appendix G of these instructions for the Stage 2 Compliance Monitoring Inventory Action Form that shows the number of  S1 and S2 locations that require DBP sampling; for example:

    - GW systems serving 100,000-499,999 population are required to collect 6 Dual samples per quarter

      - One (1) set of TTHM and HAA5 samples will be collected from the old S1 site designated DBP-1

      - Three (3) sets of TTHM and HAA5 samples will be collected from the new S2 sites designated TTHM-1, TTHM-2 and TTHM-3

      - Two (2) sets of TTHM and HAA5 samples will be collected from the new S2 sites designated HAA5-1 and HAA5-2

Sample Collection and Handling

The chemicals that comprise the total trihalomethanes (TTHMs) are considered volatile; they would rather be in the vapor or gas phase than in the aqueous phase.  This requires special consideration when collecting these samples.  Samples must be collected without any “headspace” or air in the vial.  Each lab certified to analyze these organic compounds may have a different definition of headspace.  Some may reject your samples for any air bubbles; others may allow 1 or more tiny air bubbles.  It is important to know your lab’s requirements for headspace acceptability.  Use the following techniques when collecting your TTHM samples in the twin 40-mL clear glass vials:

- Open the tap and allow the water to flow for 5 minutes

- Adjust the flow to about 500 mL (1 pint) per minute

  - Any aerator device on faucet must be removed

- Take vials out their original plastic baggies

- Open one vial

- Slowly fill the vial to the very top so that the water surface bows up and above the rim of the vial

- Re-cap the vial

- Invert the capped vial to make sure no headspace or bubbles are present

- If headspace is present then remove cap and carefully add a little more water from the tap and re-cap again

- Fill the second duplicate vial in the same manner

- Complete all lab forms and labels

- Place the two vials back into their original bag

Asbestos Sampling

Community and Non-Transient Non-Community water systems are required to collect for asbestos when the water system is known to use asbestos-cement piping as a distribution or service line or if there is a potential for asbestos contamination of the water source.  You can determine your asbestos sample requirements by referencing your PWS sample schedule on Drinking Water Watch (https://dww.water.net.env.nm.gov/DWW/) or by accessing the DWB online sampling tool.

The sample should be collected from a commonly used tap served by cement-asbestos piping and under conditions where asbestos contamination is most likely to occur.  Within distribution, this is determined by the operators mapping and or history as to where the asbestos cement piping is being used.  You may also want to discuss your DSSP asbestos sampling location(s) with your DWB CO.  Asbestos is one of the contaminants the DWB samplers were responsible for collecting prior to the January 2011 transfer of distribution system sampling to the water systems and the DWB may have record of historical asbestos sample locations.

Turbidity Monitoring

Turbidity is the clay, silt, mud or other organic/inorganic material typically present in surface waters that makes a water look cloudy.  Turbidity does not represent a health risk by itself, but because it can shield pathogens (harmful microorganisms) from disinfection processes it is considered an acute health hazard (one of three – turbidity, E.coli and nitrates).

Springs and infiltration galleries are considered surface supplies if they are found to have ground water under the direct influence of surface water (GWUDI).  The DWB will initiate a speciation study (MPA) of turbidity and microorganisms in the suspected source to determine GWUDI status.

Surface water treatment rules require that any system that uses surface water or GWUDI must provide treatment of the supply in order to meet the turbidity MCL.  Surface water or GWUDI systems must also monitor and report total organic carbon (TOC) and turbidity concentrations at source, treatment and distribution.  You can determine your TOC and turbidity monitoring and reporting requirements by referencing your PWS sample schedule on Drinking Water Watch (https://dww.water.net.env.nm.gov/DWW/) or by accessing the DWB online sampling tool.  Monitoring locations need to be identified in your DSSP.

Additional Resources:

- NMED-DWB home page can be found at https://www.env.nm.gov/dwb/index.htm

DSSP INSTRUCTIONS APPENDIX A

Disinfectant Residual Report

DSSP INSTRUCTIONS APPENDIX B

General Guidelines for Lead and Copper Site Selection, Sampling and Reporting

DSSP INSTRUCTIONS APPENDIX C

S2 DBP Sampling for GW or SW Systems Serving Less than 500 Population - One (1) DBP2 Sample per Year

NEW MEXICO

ENVIRONMENT DEPARTMENT

1277-A S. Second Street

Raton, NM  87740

Phone (575) 445-3621    Fax (575) 445-3376

www.env.nm.gov

RYAN FLYNN

Cabinet Secretary

BUTCH TONGATE

Deputy Secretary

SUSANA MARTINEZ

Governor
JOHN A. SANCHEZ
Lieutenant Governor

«Date»

«Admin_Contact_Name»

«System_Name»

«Address»

«City_», «ST» «Zip»

RE:  Stage 2 Disinfectants/Disinfection Byproducts Rule SW or GW <500 Pop Yearly Individual Sample

WSS# «WSS»

Attn: «Title» «Admin_Contact»,

On December 15, 2005 the EPA adopted the Stage 2 Disinfection Byproducts Rule (DBP2).  This rule was fully implemented on October 1, 2013 and applies to community and non-transient non-community water systems that produce and/or deliver water that is treated with a primary disinfectant (chlorine). This rule also applies to water systems that that receive some or all of their water from one or more wholesale systems which use a primary disinfectant.

Because «System_Name» water system meets one of the above criteria you are required to comply with the DBP2 rule.  The New Mexico Environment Department’s Drinking Water Bureau (NMED-DWB) has reviewed the «System_Name» water system’s previous DBP sampling data and has determined that the «System_Name» water system will be required to collect one (1) Total Trihalomethane Individual (TTHM-IND) sample per year during the month of (MONTH) beginning in 2014.   The «System_Name» water system will also be required to collect one (1) Haloacetic Acids Individual (HAA5-IND) sample per year during the month of (MONTH) beginning in 2014.  The «System_Name» water system should continue this sampling schedule until notified in writing by the NMED-DWB.

As part of the new DBP2 requirements you will be required to identify appropriate sample locations for these samples.  Please use and fill out the attached checklist to assist you in determining locations for the required samples.  This checklist will be required to be returned to the NMED-DWB no later than February 28, 2014.

DBP2 Laboratory submittal forms for the «System_Name» water system can be generated using the Samplers Application which can be accessed at the following website (https://eidea.nmenv.state.nm.us/sep/login-form).

We understand that new regulations can be difficult for public water systems. The NMED-DWB is available to assist you by phone if you have questions regarding identification of correct DBP2 Sampling Locations.  Please contact «Staff_Name» at «Staff_Phone» or at «staff_email» should you have any questions.

Sincerely,

«Staff_Name»

| STAGE 2 DISINFECTANT/DISINFECTION BYPRODUCTS SAMPLE LOCATION IDENTIFICATION CHECKLIST |  |  |
| --- | --- | --- |
| Total Trihalomethane (TTHM) Sampling location *TTHM site to represent areas in the distribution system where you expect to find higher levels of TTHM throughout the year as compared to other sites. Higher temperatures and increased residence time typically lead to higher TTHM concentrations. Low disinfectant residual usually indicates longer residence time sites |  |  |
| The «System_Name» water system has identified _____________________________as its TTHM-IND (physical address or location) sampling location. We have determined that this location is adequate based on the following criteria: Check all that are applicable This is immediately down gradient of a storage tank, which have increased residence time. This is a low water flow area, a sparsely populated area with low flow. This is a mixing zone where water from different sources combines within the distribution system. Sample sites should not be located: - At a dead-end where there are no customers - Immediately prior to booster disinfection |  |  |
| Haloacetic Acids (HAA5) Sampling Location * HAA5 site should be chosen to represent areas in the distribution system where you expect to find higher levels of HAA5 throughout the year as compared to other sites. Higher temperatures and increased residence time can lead to higher HAA5 concentrations. However, HAA5 can biodegrade when disinfectant residual levels are low or non-existent. Therefore, a high HAA5 site will not necessarily be the site with the longest residence time |  |  |
| The «System_Name» water system has identified _________________________________ as its HAA5-IND (physical address or location) sampling location. We have determined that this location is adequate based on the following criteria: Check all that are applicable This is immediately down gradient of a storage tank, which have increased residence time. This is near the ends of the distribution system, at or before the last group of customers. This is a mixing zone where water from different sources combines within the distribution system. This is prior to the last fire hydrant Sample sites should not be located: - At a dead-end where there are no customers. - Immediately prior to booster disinfection. - Where no disinfectant residual exists. - Areas with biofilm problems. |  |  |
| *I certify that I am familiar with the information contained in this report and that, to the best of my knowledge, the information is true, complete, and accurate. |  |  |
| Name of Certified Operator (Printed) | Certified Operator Signature | Date |

DSSP INSTRUCTIONS APPENDIX D

S2 DBP Sampling for GW or SW Systems Serving Less than 500 Population - One (1) TTHM and One (1) HAA5 Sample per Year

NEW MEXICO

ENVIRONMENT DEPARTMENT

1277-A S. Second Street

Raton, NM  87740

Phone (575) 445-3621    Fax (575) 445-3376

www.env.nm.gov

RYAN FLYNN

Cabinet Secretary

BUTCH TONGATE

Deputy Secretary

SUSANA MARTINEZ

Governor
JOHN A. SANCHEZ
Lieutenant Governor

«Date»

«Admin_Contact_Name»

«System_Name»

«Address»

«City_», «ST» «Zip»

RE:  Stage 2 Disinfectants/Disinfection Byproducts Rule SW or GW Pop <500 Yearly Sample

WSS# «WSS»

Attn: «Title» «Admin_Contact»,

On December 15, 2005 the EPA adopted the Stage 2 Disinfection Byproducts Rule (DBP2).  This rule was fully implemented on October 1, 2013 and applies to community and non-transient non-community water systems that produce and/or deliver water that is treated with a primary disinfectant (chlorine). This rule also applies to water systems that that receive some or all of their water from one or more wholesale systems which use a primary disinfectant.

Because «System_Name» water system meets one of the above criteria you are required to comply with the DBP2 rule.  The New Mexico Environment Department’s Drinking Water Bureau (NMED-DWB) has reviewed the «System_Name» water system’s previous DBP sampling data and has determined that the «System_Name» water system will be required to collect one (1) DBP2 sample from the distribution system per year during the month of (MONTH) beginning in 2014.  The «System_Name» water system should continue this sampling schedule until notified in writing by the NMED-DWB.

As part of the new DBP2 requirements you will be required to identify an appropriate sample location for this sample.  Please use and fill out the attached checklist to assist you in determining the location for the required sample.  This checklist will be required to be returned to the NMED-DWB no later than February 28, 2014.

DBP2 Laboratory submittal forms for the «System_Name» water system can be generated using the Samplers Application which can be accessed at the following website (https://eidea.nmenv.state.nm.us/sep/login-form).

We understand that new regulations can be difficult for public water systems. The NMED-DWB is available to assist you by phone if you have questions regarding identification of correct DBP2 Sampling Locations.  Please contact «Staff_Name» at «Staff_Phone» or at «staff_email» should you have any questions.

Sincerely,

«Staff_Name»

| STAGE 2 DISINFECTANT/DISINFECTION BYPRODUCTS SAMPLE LOCATION IDENTIFICATION CHECKLIST |  |  |
| --- | --- | --- |
| Distribution Sampling Location *Stage 2 Disinfection Byproducts site to represent areas in the distribution system where you expect to find higher levels of Disinfection Byproducts throughout the year as compared to other sites. Higher temperatures and increased residence time typically lead to higher Disinfection Byproducts concentrations. Low disinfectant residual usually indicates longer residence time sites |  |  |
| The «System_Name» water system has identified __________________________________as its (physical address or location) DBP-DIST sampling location based on the following criteria: Check all that are applicable This is immediately down gradient of a storage tank, which have increased residence time. This is a low water flow area, a sparsely populated area with low flow. This is a mixing zone where water from different sources combines within the distribution system. This is immediately down gradient of a storage tank, which have increased residence time. This is near the ends of the distribution system, at or before the last group of customers. This is prior to the last fire hydrant Sample sites should not be located: - At a dead-end where there are no customers - Immediately prior to booster disinfection - Where no disinfectant residual exists. - Areas with biofilm problems. |  |  |
| *I certify that I am familiar with the information contained in this report and that, to the best of my knowledge, the information is true, complete, and accurate. |  |  |
| Name of Certified Operator (Printed) | Certified Operator Signature | Date |

DSSP INSTRUCTIONS APPENDIX E

GW Systems Serving 500-9999 Population - One (1) TTHM-1 Dual and One (1) HAA5-1 Dual Sample per Year

NEW MEXICO

ENVIRONMENT DEPARTMENT

1277-A S. Second Street

Raton, NM  87740

Phone (575) 445-3621    Fax (575) 445-3376

www.env.nm.gov

RYAN FLYNN

Cabinet Secretary

BUTCH TONGATE

Deputy Secretary

SUSANA MARTINEZ

Governor
JOHN A. SANCHEZ
Lieutenant Governor

«Date»

«Admin_Contact_Name»

«System_Name»

«Address»

«City_», «ST» «Zip»

RE:  Stage 2 Disinfectants/Disinfection Byproducts Rule GW 500-9999 Yearly Dual Sample

WSS# «WSS»

Attn: «Title» «Admin_Contact»,

On December 15, 2005 the EPA adopted the Stage 2 Disinfection Byproducts Rule (DBP2).  This rule was fully implemented on October 1, 2013 and applies to community and non-transient non-community water systems that produce and/or deliver water that is treated with a primary disinfectant (chlorine). This rule also applies to water systems that that receive some or all of their water from one or more wholesale systems which use a primary disinfectant.

Because «System_Name» water system meets one of the above criteria you are required to comply with the DBP2 rule.  The New Mexico Environment Department’s Drinking Water Bureau (NMED-DWB) has reviewed the «System_Name» water system’s previous DBP sampling data and has determined that the «System_Name» water system will be required to collect one (1) Total Trihalomethane Dual (TTHM-1) sample per year during the month of (MONTH) beginning in 2014.   The «System_Name» water system will also be required to collect one (1) Haloacetic Acids Dual (HAA5-1) sample per year during the month of (MONTH) beginning in 2014.  The «System_Name» water system should continue this sampling schedule until notified in writing by the NMED-DWB.

As part of the new DBP2 requirements you will be required to identify appropriate sample locations for these samples.  Please use and fill out the attached checklist to assist you in determining locations for the required samples.  This checklist will be required to be returned to the NMED-DWB no later than February 28, 2014.

DBP2 Laboratory submittal forms for the «System_Name» water system can be generated using the Samplers Application which can be accessed at the following website (https://eidea.nmenv.state.nm.us/sep/login-form).

We understand that new regulations can be difficult for public water systems. The NMED-DWB is available to assist you by phone if you have questions regarding identification of correct DBP2 Sampling Locations.  Please contact «Staff_Name» at «Staff_Phone» or at «staff_email» should you have any questions.

Sincerely,

«Staff_Name»

| STAGE 2 DISINFECTANT/DISINFECTION BYPRODUCTS SAMPLE LOCATION IDENTIFICATION CHECKLIST |  |  |
| --- | --- | --- |
| Total Trihalomethane (TTHM) Sampling location *TTHM site to represent areas in the distribution system where you expect to find higher levels of TTHM throughout the year as compared to other sites. Higher temperatures and increased residence time typically lead to higher TTHM concentrations. Low disinfectant residual usually indicates longer residence time sites |  |  |
| The «System_Name» water system has identified _____________________________as its TTHM-1 (physical address or location) sampling location. We have determined that this location is adequate based on the following criteria: Check all that are applicable This is immediately down gradient of a storage tank, which have increased residence time. This is a low water flow area, a sparsely populated area with low flow. This is a mixing zone where water from different sources combines within the distribution system. Sample sites should not be located: - At a dead-end where there are no customers - Immediately prior to booster disinfection |  |  |
| Haloacetic Acids (HAA5) Sampling Location * HAA5 site should be chosen to represent areas in the distribution system where you expect to find higher levels of HAA5 throughout the year as compared to other sites. Higher temperatures and increased residence time can lead to higher HAA5 concentrations. However, HAA5 can biodegrade when disinfectant residual levels are low or non-existent. Therefore, a high HAA5 site will not necessarily be the site with the longest residence time |  |  |
| The «System_Name» water system has identified _________________________________ as its HAA5-1 (physical address or location) sampling location. We have determined that this location is adequate based on the following criteria: Check all that are applicable This is immediately down gradient of a storage tank, which have increased residence time. This is near the ends of the distribution system, at or before the last group of customers. This is a mixing zone where water from different sources combines within the distribution system. This is prior to the last fire hydrant Sample sites should not be located: - At a dead-end where there are no customers. - Immediately prior to booster disinfection. - Where no disinfectant residual exists. - Areas with biofilm problems. |  |  |
| *I certify that I am familiar with the information contained in this report and that, to the best of my knowledge, the information is true, complete, and accurate. |  |  |
| Name of Certified Operator (Printed) | Certified Operator Signature | Date |

DSSP INSTRUCTIONS APPENDIX F

SW Systems Serving 500-3300 Population - One (1) TTHM-IND and One (1) HAA5-IND Sample per Quarter

NEW MEXICO

ENVIRONMENT DEPARTMENT

1277-A S. Second Street

Raton, NM  87740

Phone (575) 445-3621    Fax (575) 445-3376

www.env.nm.gov

«Date»

«Admin_Contact_Name»

«System_Name»

«Address»

«City_», «ST» «Zip»

RE:  Stage 2 Disinfectants/Disinfection Byproducts Rule SW 500-3300 Quarterly Individual Sample

WSS# «WSS»

Attn: «Title» «Admin_Contact»,

On December 15, 2005 the EPA adopted the Stage 2 Disinfection Byproducts Rule (DBP2).  This rule was fully implemented on October 1, 2013 and applies to community and non-transient non-community water systems that produce and/or deliver water that is treated with a primary disinfectant (chlorine). This rule also applies to water systems that that receive some or all of their water from one or more wholesale systems which use a primary disinfectant.

Because «System_Name» water system meets one of the above criteria you are required to comply with the DBP2 rule.  The New Mexico Environment Department’s Drinking Water Bureau (NMED-DWB) has reviewed the «System_Name» water system’s previous DBP sampling data and has determined that the «System_Name» water system will be required to collect one (1) Total Trihalomethane Individual (TTHM-IND) sample during the months of (January, April, July, & October) (February, May, August, & November) (March, June, September, & December) beginning in 2014.   The «System_Name» water system will also be required to collect one (1) Haloacetic Acids Individual (HAA5-IND) sample during the months of (January, April, July, & October) (February, May, August, & November) (March, June, September, & December) beginning in 2014.    The «System_Name» water system should continue this sampling schedule until notified in writing by the NMED-DWB.

As part of the new DBP2 requirements you will be required to identify appropriate sample locations for these samples.  Please use and fill out the attached checklist to assist you in determining locations for the required samples.  This checklist will be required to be returned to the NMED-DWB no later than February 28, 2014.

DBP2 Laboratory submittal forms for the «System_Name» water system can be generated using the Samplers Application which can be accessed at the following website (https://eidea.nmenv.state.nm.us/sep/login-form).

We understand that new regulations can be difficult for public water systems. The NMED-DWB is available to assist you by phone if you have questions regarding identification of correct DBP2 Sampling Locations.  Please contact «Staff_Name» at «Staff_Phone» or at «staff_email» should you have any questions.

Sincerely,

«Staff_Name»

| STAGE 2 DISINFECTANT/DISINFECTION BYPRODUCTS SAMPLE LOCATION IDENTIFICATION CHECKLIST |  |  |
| --- | --- | --- |
| Total Trihalomethane (TTHM) Sampling location *TTHM site to represent areas in the distribution system where you expect to find higher levels of TTHM throughout the year as compared to other sites. Higher temperatures and increased residence time typically lead to higher TTHM concentrations. Low disinfectant residual usually indicates longer residence time sites |  |  |
| The «System_Name» water system has identified _____________________________as its TTHM-IND (physical address or location) sampling location. We have determined that this location is adequate based on the following criteria: Check all that are applicable This is immediately down gradient of a storage tank, which have increased residence time. This is a low water flow area, a sparsely populated area with low flow. This is a mixing zone where water from different sources combines within the distribution system. Sample sites should not be located: - At a dead-end where there are no customers - Immediately prior to booster disinfection |  |  |
| Haloacetic Acids (HAA5) Sampling Location * HAA5 site should be chosen to represent areas in the distribution system where you expect to find higher levels of HAA5 throughout the year as compared to other sites. Higher temperatures and increased residence time can lead to higher HAA5 concentrations. However, HAA5 can biodegrade when disinfectant residual levels are low or non-existent. Therefore, a high HAA5 site will not necessarily be the site with the longest residence time |  |  |
| The «System_Name» water system has identified _________________________________ as its HAA5-IND (physical address or location) sampling location. We have determined that this location is adequate based on the following criteria: Check all that are applicable This is immediately down gradient of a storage tank, which have increased residence time. This is near the ends of the distribution system, at or before the last group of customers. This is a mixing zone where water from different sources combines within the distribution system. This is prior to the last fire hydrant Sample sites should not be located: - At a dead-end where there are no customers. - Immediately prior to booster disinfection. - Where no disinfectant residual exists. - Areas with biofilm problems. |  |  |
| *I certify that I am familiar with the information contained in this report and that, to the best of my knowledge, the information is true, complete, and accurate. |  |  |
| Name of Certified Operator (Printed) | Certified Operator Signature | Date |

DSSP INSTRUCTIONS APPENDIX G

Stage 2 DBP Compliance Monitoring Inventory Action Form

The template begins on the next page.

<Highlighted text is either general information or are suggestions that need to be modified to reflect system-specific conditions or information or deleted if they do not apply >

TITLE PAGE

DRINKING WATER DISTRIBUTION SYSTEM

SAMPLING PLAN (DSSP) FOR:

WATER SYSTEM NAME

PWS # NM35-XXX-XX

Address City Zip

Phone Email

County

Original Plan Prepared By Name & Title

Preparer’s Contact Info

Date Prepared

Date Submitted to NMED DWB

Signature

Reviewed by DWB SWIG Tech Services Coordinator Name

Date Recommended for Approval

Signature

INITIAL DSSP SECTION APPROVALS

| Approved Not-Approved Approved | RTCR and GWR Bacteriological Sampling Compliance Officer Signature: ________________________ |
| --- | --- |
| Approved Not-Approved Not Applicable | Disinfectant Residual Monitoring Compliance Officer Signature: ________________________ |
| Approved Not-Approved Not Applicable | Lead and Copper Rule (LCR) Sampling Rule Administrator Signature: ________________________ |
| Approved Not-Approved Not Applicable | Disinfectants/Disinfection By-Products Rule (D/DBP) Sampling Rule Administrator Signature: ________________________ |
| Approved Not-Approved Not Applicable | Entry Point (EP) Chemical Compliance Sampling for Organics, Inorganics and Radiologicals Compliance Officer Signature: ________________________ |
| Approved Not-Approved Not Applicable | Distribution System Asbestos Sampling Compliance Officer Signature: ________________________ |

REVISION TRACKING

Original Plan Prepared By

Date Prepared

1st Revision By

1st Revision Date

Date Submitted to NMED

Date Approved by NMED

2nd Revision By

2nd Revision Date

Date Submitted to NMED

Date Approved by NMED

TABLE OF CONTENTS

Page

Title Page

Revision Tracking

Table of Contents

Section 1	System Description and Contact Information

Section 2	RTCR and GWR Bacteriological Sampling

Section 3 	Disinfectant Residual Monitoring

Section 4	Lead and Copper Rule (LCR) Sampling

Section 5 	Disinfectants/Disinfection By-Products Rule (D/DBP) Sampling

Section 6	Entry Point (EP) Chemical Compliance Sampling for Organics, Inorganics and Radiologicals

Section 7	Distribution System Asbestos Sampling

Appendices

Appendix A	System Sample Schedule from Drinking Water Watch

Appendix B RTCR Sample Sites Spreadsheet

Spreadsheet Submittal Acknowledgement Form

Appendix C	Map(s) of Distribution System Showing:

RTCR Routine Sample Sites

RTCR Repeat Sample Sites

RTCR Seasonal Start-Up Special Sample Sites (if a seasonal system)

GWR Triggered Source Sample Sites

Chlorine Residual Monitoring Sites (if a chlorinated system)

Lead and Copper Sample Sites (if required)

D/DBP Sample Sites (if a chlorinated system)

Asbestos (if required)

Appendix D	Alternate RTCR Repeat Sampling Sites SOP

Appendix E	Disinfectant Residual Measurement Sampling Report

Appendix F	Guidelines for Lead and Copper Site Selection and Sampling

Suggested Directions to Homeowners for Sample Collection

Section 1:  System Description and Contact Information

The <Water System> owns and operates one groundwater well. The water system serves 125 people with 70 connections.  Water from the well is disinfected with a 6% hypochlorite solution prior to being pumped to a 10,000 gallon ground storage tank.  Water from the tank gravity flows to our distribution system.

Our current sample schedule from Drinking Water Watch is provided in Appendix A.

| Administrative Contact: | name |
| --- | --- |
|  | Address city state zip |
|  | Phone(s) |
|  | email |
| Certified Operator: | name |
|  | Address city state zip |
|  | Phone(s) email |
| NMED-DWB Contact | Compliance Officer (CO) name Address city state zip Phone(s) email |

Example System Schematic

CHLORINE

INJECTION

WELL #1

ENTRY POINT

SAMPLE PORT

DISTRIBUTION SYSTEM

RAW WATER		10,000 GALLON

SAMPLING PORT 	STORAGE TANK

Section 2:  Bacteriological Sampling

Revised Total Coliform Rule (RTCR) Sampling

Frequency

Based on our population of X and the sample requirements provided in Tables 1 and 2 of the instructions, we are required to designate a minimum of Y routine sample locations per month and collect a minimum of Z routine bacteriological samples per month.

Location

We are required to identify each of our routine monthly bacteriological sample locations, and the three (3) repeat sites (original, up- and downstream) associated with each routine site with either a physical address or physical location.  Those addresses/physical locations are listed on the RTCR Sample Site spreadsheet in Appendix B.  That spreadsheet has been submitted to the DWB according to the instructions that accompanied the spreadsheet; the submittal acknowledgement is included in Appendix B.

Appendix C includes the map(s) showing where these routine and repeat sites are located throughout our distribution system.

We understand that the DWB will be verifying that we sample from each routine and repeat sample location designated on our DSSP.  We further understand that our DWB Compliance Officer will also verify that we collect the routine samples at regular intervals from month to month (i.e., same week each month) and that we are rotating through each major and minor portion of the distribution system.

Alternate Repeat Sampling Locations

The RTCR Sample Site Spreadsheet in Appendix B designates repeat sample locations that are within the five (5) connections up- and downstream of the original routine sample location.  However, we understand that we can use alternate up- or downstream repeat sampling locations that are outside the five (5) connections from the original sample site as long as we submit a Standard Operating Procedure (SOP) that specifies our criteria for selecting these alternate repeat sampling sites on a situational basis (i.e., for any time we are required to collect repeat distribution system samples and determine that the prescribed repeat locations do not adequately identify potential pathways of contamination).

We do not plan to use any alternate repeat sampling sites. OR

We do plan to use alternate repeat sampling sites, and our SOP is provided in Appendix D.  The SOP has been designed to focus the repeat samples at locations that best verify and determine the extent of potential contamination of the distribution system area based on specific situations; however, we understand that the DWB may modify the SOP or require other alternate monitoring locations as needed.

Seasonal Systems

Seasonal systems are systems that start up and shut down at the beginning and end of a specific operating season and may depressurize all or part of the water system at some point during the year.

We are not a seasonal system. OR

We are a seasonal system, and as such, we are required to follow the DWB Seasonal System Start-up Procedure and submit our Seasonal Start-up Procedure Checklist to our CO at least 10 days prior to opening.  The start-up procedure will require us to collect one or more Special bacteriological samples to verify water quality.

Special samples will be taken at the X sites listed in the table below which identifies the physical address or location of the Special sample and the system feature (i.e., storage tank, distribution system) the sample is associated with along with the Special sample number.  These sites were chosen based on the requirements established in the seasonal start-up guidance provided by the DWB.  They are also designated on the distribution system map(s) in Appendix C.  We further understand that Special samples are samples collected and paid for by the water system.

<insert table here>

Groundwater Rule (GWR) Sampling

One (1) Triggered Source Water sample is required to be collected from every active well if any of our routine monthly samples test positive for Total Coliform (TC) or E.Coli (EC). These Triggered Source Water Samples will be collected directly from each of our wells prior to any treatment and are shown on the map(s) in Appendix C.  Our sample points are labeled as “Raw Water” as shown in the photograph below.

<insert photo here>

<example photo>

Sampling Requirements

New Mexico Regulations require that a certified sampler or certified operator collect the RTCR and GWR samples.  Because of this requirement, our certified <sampler/operator> will be required to collect our bacteriological samples.  Once collected, our <sampler/operator> will submit the samples and their Chain-of-Custody (CoC) forms to the following certified laboratory within 24 hours of the sample being collected:

laboratory name

address

city state zip

phone(s)

Compliance Status

RTCR

Our water system triggers an assessment with the RTCR if:

- We get 2 or more TC+ samples in any one (1) month (for systems that take <40 samples/month);

- >5% of our routine samples are TC+ (for systems that take 40 or more samples/month;

- We fail to take all the required repeat samples

- Any one (1) of these conditions will trigger a required Level 1 assessment/correction action

A Level 2 assessment/corrective action is triggered if we get:

- An EC Maximum Contaminant Level (MCL) violation; or

- An EC monitoring violation; or

- We trigger two (2) Level 1 assessments within a rolling 12 month period

GWR

We are in compliance with the GWR if our Triggered Source Water sample(s) are free of EC.

We will immediately notify our DWB CO if any of our Triggered Source Water samples test positive for TC or EC.  At that time, we can be required to conduct additional sampling, correct significant deficiencies, or disinfect our water to meet 4-log treatment requirements.

Section 3:  Disinfectant Residual Monitoring

Frequency

We do not add chlorine to our water, and as such we are not required to monitor chlorine residual. OR

We are a chlorinated system, and as such we are required to measure chlorine residuals at the same time we collect our monthly routine RTCR samples.  We also measure chlorine residuals throughout the month as part of our best management practices.

Based on our population of X and the requirements provided in Tables 1 and 2 of the DSSP template instructions, we are required to designate a minimum of Y chlorine residual monitoring locations per month.

Location

Chlorine residuals are measured at the same time and from the same locations where we collect our routine monthly RTCR samples.  Results are recorded on each bacteriological CoC form and submitted to the lab with those samples.  The sites were chosen based on the fact that they are representative of the entire distribution system, and are designated on the map(s) included in Appendix C.

We also measure chlorine residuals at the Y chlorine residual monitoring sites throughout the month as part of our best management practices.  This is to ensure that injection dosages are sufficient to meet chlorine demand and maintain adequate residuals in the entire distribution system, including vulnerable portions of the system.  Vulnerable areas are anywhere we might have increased water age or stagnant water (storage tanks, high elevation/low pressure, low occupancy, dead ends).  We use these chlorine residual results along with other information to focus our best management practices such as line and hydrant flushing (along with valve exercising).

Methodology and Reporting

Our certified <operator/sampler> uses a <specify equipment here> to measure chlorine residuals and follows all sample collection, handling, measuring and equipment calibration protocol specified in the operation manual.

All chlorine residuals that are measured during RTCR routine and repeat sampling and for best management practices.  These results are required to be recorded on the bacteriological chain of custody  forms that are submitted to the lab and are also recorded on the Residual Disinfectant Residual Measurement Sampling Report (Appendix E).  We submit this report to our DWB CO by the 10th day following each quarter, as required.

Compliance

Our water system is in compliance if:

- We maintain chlorine residuals less than or equal to 4.0 mg/L, the Maximum Residual Disinfectant Limit (MRDL)

- We submit our Residual Disinfectant Residual Measurement Sampling Report to our DWB CO no later than the 10th day following each quarter

Section 4:  Lead and Copper Rule (LCR) Sampling

Frequency

We are required to collect five (5) Lead and Copper samples once every three (3) years.  We use Drinking Water Watch to keep track of this sampling schedule (Appendix A).

Location

Sample locations are based on the age and types of structures we have in our community, including schools.  We have included guidelines for site selection and sampling in Appendix F of this plan.  Based on these criteria we have selected the main and alternate locations designated in the following table for every Lead and Copper sampling event.  These locations are also designated on the map(s) in Appendix C.

| Site Number | Address |
| --- | --- |
| 1 | 246 Even Parkway |
| 2 | 135 Odd Street |
| 3 | 888 Water Way |
| 4 | 753 Turkey Road |
| 5 | 525 Marquez St |
| <6> | <add more rows for additional samples as required> |
| Alternate Sites |  |
| ALT | 2506 46th Street |
| ALT | 8616 Coral Drive |
| ALT | 225 Vincent St |
| <ALT> | <add more rows for additional alt sites as needed> |

Methodology

Sampling protocol requires that these samples are:

- Point-of-Use (POU) collected directly from the customer’s tap

- Collected as a “first draw” sample before any other usage takes place at the sampling tap (no flushing of faucet or lines before collection)

- 6 to 18 hours old in customer’s plumbing

- Typically collected by occupant of sampling location

- Typically collected during third quarter warm weather months July to September

In order to meet these sampling protocol our certified <sampler/operator> will obtain appropriate sample containers and CoC forms, deliver containers and forms to sample location occupants and provide instruction for sample collection (also included in Appendix F), arrange for sample pick-up after sampling, complete CoC forms, and submit samples to the following appropriate certified laboratory:

laboratory name

address

city state zip

phone(s)

Compliance

Our water system is in compliance if we collect our Lead and Copper samples according to schedule and the sample results are below the 90th Percentile Action Level for each contaminant (Copper=1.3 mg/L, Lead=0.015 mg/L).  We will notify our DWB CO of any violations; the DWB may require additional sampling.

Section 5:  Disinfectants/Disinfection By-Products (D/DBP) Rule Sampling

Frequency and Location

Stage 2 Disinfectants/Disinfection By-Products Rule (S2D/DBPR) sampling requirements are based on system size (population served) and type (CWS/NTNC, GW/SW).  Since we are a <GW/SW> system that serves a population of X people we are required to collect # Total Trihalomethane (TTHM) samples and # Haloacetic Acid (HAA5) samples <annually/quarterly> from our distribution system.  We use Drinking Water Watch to keep track of this sampling schedule (Appendix A).

Specifically, we have been instructed by the DWB to collect our DBP samples as follows:

<choose one>:

Certain GW or SW systems serving less than 500 population:

Facility ID #xxxxx000, Sample Point ID #DBP-DIST Dual

[Collect one TTHM AND one HAA5 sample per year from same site]

OR

Other GW or SW systems serving less than 500 population:

Facility ID #xxxxx000, Sample Point ID #TTHM-IND

[Collect one TTHM sample per year at one site]

Facility ID #xxxxx000, Sample Point ID #HAA5-IND

[Collect one HAA5 sample per year at another site]

OR

GW systems serving 500-9999 population:

Facility ID #xxxxx000, Sample Point ID #TTHM-1 Dual and #HAA5-1 Dual

[Collect one TTHM sample AND one HAA5 sample per year at two (2) different sites]

OR

SW systems serving 500-3300 population:

Facility ID #xxxxx000, Sample Point ID #TTHM-IND

[Collect one (1) TTHM sample per quarter at one site]

Facility ID #xxxxx000, Sample Point ID #HAA5-IND

[Collect one (1) HAA5 sample per quarter at another site]

OR

SW systems serving 3301-9999 population:

Facility ID #xxxxx000, Sample Point ID #TTHM-1 Dual and #HAA5-1 Dual

[Collect one TTHM sample AND one HAA5 sample per quarter at two (2) different sites]

OR

All other GW and SW systems serving 10,000 population or greater:

[Collect anywhere from 4 to 20 Dual TTHM and HAA5 samples per quarter; both TTHM and HAA5 samples are collected at the same time and location quarterly]

Our S2D/DBP sample locations are designated on the map(s) in Appendix C.

Sampling Method

The chemicals that comprise the total trihalomethanes (TTHMs) are considered volatile; they would rather be in the vapor or gas phase than in the aqueous phase.  This requires special consideration when collecting these samples.  Our certified <sampler/operator> will collect the TTHM samples without any “headspace” or air in the vial using the following techniques:

- Open the tap and allow the water to flow for 5 minutes

- Adjust the flow to about 500 mL (1 pint) per minute

  - Any aerator device on faucet must be removed

- Take twin 40-mL vials out their original plastic baggies

- Open one vial

- Slowly fill the vial to the very top so that the water surface bows up and above the rim of the vial

- Re-cap the vial

- Invert the capped vial to make sure no headspace or bubbles are present

- If headspace is present then remove cap and carefully add a little more water from the tap and re-cap again

- Fill the second duplicate vial in the same manner

- Complete all lab CoC forms and labels

- Place the two vials back into their original bag

HAA5 vials can be filled with headspace since the chemical is not volatile.

Samples will be submitted to the following appropriate certified laboratory:

laboratory name

address

city state zip

phone(s)

Compliance

Our water system is in compliance if we meet the required sampling schedule and the locational running annual average (LRAA) is less than the MCL for each D/DBP (TTHM=80ug/L, HAA5=60ug/L).  We are required to, and will notify our DWB CO of any violations.

Section 6:  Entry Point (EP) Chemical Compliance Sampling for Organics, Inorganics & Radiologicals

Frequency

Chemical samples are collected at a time frame and frequency that is established by the DWB.  We keep track of our sampling schedules (Appendix A) for all SDWA primary drinking water contaminants using the DWB Drinking Water Watch website.

Location

These chemical compliance samples are required to be taken at the Entry Point (EP) to the distribution system, regulatorily defined as where potable water is first made available to our customers.  Our EP sample point is a frost free hydrant that is located on the downstream side of our storage tank as shown in the following photograph:

<insert photo here>

<example photo>

Sampling Method

We are subject to Conservation Fund payments to NM Taxation and Revenue at a rate of $0.03 per thousand gallons produced per month, and as such DWB staff samplers collect our EP chemical compliance samples.  They are responsible for arranging a visit with us for access to the EP, properly collecting the samples, filling out CoC forms and submitting the samples to an appropriate certified laboratory for analysis.  However, we do understand that we are ultimately responsible for the collection of these samples.  If the DWB staff sampler has not arranged for their collection within one (1) month of their due date we will either contact the DWB to remind them that the sample(s) must be collected or we will arrange for a certified sampler or operator to collect the samples and submit them to a certified laboratory.

OR

We are a <federal/Tribal> facility and NOT subject to Conservation Fund payments.  Consequently, we are responsible for our own EP chemical compliance sampling according to the DWB sample schedule (Appendix A).  Our certified <sampler/operator> collects our EP chemical compliance samples and submits the samples and completed CoC forms to the following appropriate certified laboratory(s) for analysis:

laboratory name(s)

address

city state zip

phone(s)

Compliance

Our water system is in compliance if the EP chemical compliance samples are collected according to schedule and chemical concentrations meet all the MCL requirements set forth by the SDWA primary drinking water standards.   We are required to, and will notify our DWB CO of any violations and follow all Public Notification Rule and other regulatory requirements in the event of any MCL, sampling or reporting violations.

Section 7:  Distribution System Asbestos Sampling

Frequency

We have reviewed our sample schedule on Drinking Water Watch (included in Appendix A) and verified that we are <not> required to sample our distribution system for asbestos.

Location (if applicable)

Refer to the map(s) in Appendix C for asbestos sample locations.

Sampling Method (if applicable)

Our certified <sampler/operator> will obtain appropriate sample containers and CoC forms, collect the sample(s), complete CoC forms, and submit samples to the following appropriate certified laboratory:

laboratory name

address

city state zip

phone(s)

Compliance (if applicable)

Our water system is in compliance if we meet the required sampling schedule and the sample results meet the asbestos MCL of 7,000,000 fibers/L.  We are required to, and will notify our DWB CO of any violations.

APPENDIX A

System Sample Schedule from Drinking Water Watch

APPENDIX B

RTCR Sample Sites Spreadsheet

Spreadsheet Submittal Acknowledgement Form

Appendix C

Map(s) of Distribution System Showing:

RTCR Routine Sample Sites

RTCR Repeat Sample Sites

RTCR Seasonal Start-Up Special Sample Sites (if a seasonal system)

GWR Triggered Source Sampling Sites

Chlorine Residual Monitor Sites (if a chlorinated system)

Lead and Copper Sample Sites (if required)

D/DBP Sample Sites (if a chlorinated system)

Asbestos (if required)

APPENDIX D

Alternate RTCR Repeat Sampling Sites SOP

APPENDIX E

Disinfectant Residual Report

APPENDIX F

Guidelines for Lead and Copper Site Selection and Sampling

Suggested Directions to Homeowners for Sample Collection